## Instructions
Water Distribution Network Solver — Hardy-Cross Method
Blackwood Meadows Subdivision, Waterloo, ON (fictional/synthetic network for portfolio use)
PURPOSE
This workbook is the input/output interface for a MATLAB script (hardy_cross_solver.m) that solves
flow distribution and pressure in a looped municipal watermain network using the Hardy-Cross method.
HOW TO USE
1. Edit values in the 'Node_Data' and 'Pipe_Data' sheets (yellow-shaded cells) to change the network.
2. Run hardy_cross_solver.m in MATLAB with this file in the same folder.
3. The script reads the two input sheets, solves the network, and writes results into 'Results'.
4. Do not rename sheet tabs or column headers — the MATLAB script reads them by name.
NETWORK LAYOUT (grid reference)
N1(source) --P1-- N2 --P2-- N3
¦ ¦ ¦
P3 P4 P5
¦ ¦ ¦
N4 --P6-------- N5 --P7-- N6
¦
P8
¦
N7 (cul-de-sac / dead end)
DESIGN CRITERIA (Ontario MECP Design Guidelines for Drinking Water Systems)
- Minimum residual pressure: 275 kPa (40 psi) at max-day demand
- Maximum design velocity: 2.5 m/s
Both are checked automatically and flagged PASS/FAIL in the Results sheet.
METHOD NOTES
- Head loss uses the Hazen-Williams equation (SI units): hf = 10.67 * L * Q^1.852 / (C^1.852 * D^4.8704)
- Loop flow correction each iteration: dQ = -(sum of signed head loss around loop) / (1.852 * sum(hf/Q))
- Convergence when the largest ¦dQ¦ across all loops is below 1e-7 m3/s, or after a maximum of 50 iterations.
- The initial flow guess (in the solver code) already satisfies continuity at every node; if you change
demands or add pipes, update the initial guess in the script so continuity still balances before iterating.
ASSUMPTIONS
- All demands are steady-state average-day demand (no fire flow or peak hour case included).
- Source node N1 has a fixed hydraulic grade line (HGL), representing an elevated tank or a fixed-pressure
connection to the municipal trunk main.
- Pipe material assumed PVC watermain, Hazen-Williams C = 130 (typical new-pipe OPSS value).
FIRE FLOW SCENARIO
A second run adds a fire demand at N7 (the hydraulically most remote node) on top of its average-day
demand, using a typical FUS minimum required fire flow for a single-family residential subdivision
(~4,000 L/min = 66.7 L/s). Set in the Fire_Demand_Ls column of Node_Data. Minimum residual pressure
during fire flow drops to 140 kPa (20 psi) per Ontario MECP guidance, vs. 275 kPa for average-day demand.
Results are written to the Results_FireFlow sheet.
AGED-PIPE SENSITIVITY SCENARIO
A third run repeats the average-day case with Hazen-Williams C reduced from 130 to 100 for every pipe,
representing ~20+ years of tuberculation/roughening in unlined pipe. This shows how much pressure margin
erodes as the network ages, without changing demands or topology. Results are written to Results_Sensitivity.
LIMITATIONS
This is a simplified teaching/portfolio model, not a substitute for professional network modelling software
(e.g. EPANET, Bentley WaterGEMS), which solve the full nodal system simultaneously via the global gradient
algorithm rather than loop-by-loop like Hardy-Cross. The network here is synthetic (not tied to real GIS or
SCADA data), demands are static average-day/fire-flow snapshots rather than a diurnal demand pattern, and
minor losses (fittings, valves) are neglected. These simplifications are appropriate for a portfolio
demonstration of the method but would need to be addressed before use on an actual design.

## Node_Data
Node_ID | Description | Type | Elevation_m | Demand_Ls | Fixed_HGL_m | Fire_Demand_Ls
N1 | Source - elevated tank tie-in | Source | 330 |  | 385
N2 | Maple Grove Ct - block A | Demand | 328.5 | 8.5 |  | 0
N3 | Cedarhollow Ave - block A | Demand | 327 | 6 |  | 0
N4 | Birchwood Dr - block B | Demand | 331 | 7 |  | 0
N5 | Willowmere St - block B | Demand | 329.5 | 9 |  | 0
N6 | Ashbury Ln - block B | Demand | 326.5 | 5.5 |  | 0
N7 | Thornebury Ct - cul-de-sac | Demand | 332 | 3 |  | 66.7
Fire demand applied at the hydraulically most remote node (N7) per FUS guideline (~4,000 L/min min. required fire flow, residential).

## Pipe_Data
Pipe_ID | From_Node | To_Node | Length_m | Diameter_mm | Hazen_Williams_C | Description
P1 | N1 | N2 | 200 | 250 | 130 | Feeder main - Maple Grove
P2 | N2 | N3 | 180 | 200 | 130 | Distribution - Cedarhollow
P3 | N1 | N4 | 220 | 250 | 130 | Feeder main - Birchwood
P4 | N2 | N5 | 150 | 150 | 130 | Cross-connector
P5 | N3 | N6 | 170 | 150 | 130 | Distribution - Ashbury
P6 | N4 | N5 | 160 | 200 | 130 | Distribution - Willowmere
P7 | N5 | N6 | 190 | 200 | 130 | Cross-connector
P8 | N4 | N7 | 140 | 150 | 130 | Cul-de-sac branch - Thornebury

## Results
Results are written here automatically by hardy_cross_solver.m — do not edit by hand.
NODE RESULTS | [5 empty] | PIPE RESULTS
Node_ID | Elevation_m | HGL_m | Pressure_kPa | Pressure_psi | Min_Pressure_Check | Pipe_ID | Flow_Ls | Velocity_ms | Headloss_m | Velocity_Check

## Results_FireFlow
Fire-flow scenario results, written by hardy_cross_solver.m — do not edit by hand. Min pressure check uses 140 kPa (fire flow) instead of 275 kPa.
NODE RESULTS | [5 empty] | PIPE RESULTS
Node_ID | Elevation_m | HGL_m | Pressure_kPa | Pressure_psi | Min_Pressure_Check | Pipe_ID | Flow_Ls | Velocity_ms | Headloss_m | Velocity_Check

## Results_Sensitivity
Aged-pipe sensitivity results (Hazen-Williams C=100), written by hardy_cross_solver.m — do not edit by hand.
NODE RESULTS | [5 empty] | PIPE RESULTS
Node_ID | Elevation_m | HGL_m | Pressure_kPa | Pressure_psi | Min_Pressure_Check | Pipe_ID | Flow_Ls | Velocity_ms | Headloss_m | Velocity_Check